Loading program on M241
TURN THE POWER OFF AT 1CB
INSERT THE SDHC CARD
TURN THE POWER ON
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 INITIAL LIGHTS WHEN POWER IS TURNED ON


[image: Graphical user interface

Description automatically generated] 
WHEN THE SD LIGHT COMES ON
THE PROGRAM IS LOADED
TURNOFF THE POWER AT 1CB
REMOVE THE SD CARD
TURN THE POWER BACK ON AT 1CB
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INTIAL LIGHT WHEN POWER IS TURNED ON
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THEN THE ERR LIGHT COMES ON

[image: PROGRAM DONE LOADING WHEN RUN AND ETH LIGHTS ARE ON AND THE SL2 LIGHT IS FLASHING
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WHEN THE RUN AND ETH LIGHTS COME ON AND THE SL2 LIGHT IS FLASHING THE M241 IS GOOD TO GO.
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