Loading program on M241

TURN THE POWER OFF AT 1CB

INSERT THE SDHC CARD

TURN THE POWER ON

INITIAL LIGHTS WHEN POWER IS TURNED ON

WHEN THE SD LIGHT COMES ON

THE PROGRAM IS LOADED

TURNOFF THE POWER AT 1CB

REMOVE THE SD CARD

TURN THE POWER BACK ON AT 1CB

INTIAL LIGHT WHEN POWER IS TURNED ON

THEN THE ERR LIGHT COMES ON

WHEN THE RUN AND ETH LIGHTS COME ON AND THE SL2 LIGHT IS FLASHING THE M241 IS GOOD TO GO.